## Slide 1: Village of Pinckney SAW Grant
EGLE Project No. 1681-01

## Slide 2: Grantee Information
Village of Pinckney
Project Grant Amount: $300,946
Applicant Match Amount: $33,439
Total: $334,385

## Slide 3: Asset Management Plan Goals
Provide Opinion of Asset Conditions and Future Needs
Review O, M, & R Costs to provide a defined Level of Service (LOS)
Use System-Wide-Information to determine the lowest life-cycle cost to maintain LOS
To perform pre-emptive maintenance on the system before they become emergencies

## Slide 4: Wastewater Asset Inventory
Condition Assessment
  Gravity Sewer Cleaning and Televising
  Field Surveying
  Physical Site Observations

## Slide 5: System Asset Summary
Table 1.2 - System Asset Summary |  | 
Total Gravity Sewer | 58,487 | Feet
Total Force‐Main Sewer | 5,892 | Feet
Total Manholes | 245 | Each
Pump/Lift Stations | 4 | Each
WWTP | 1 | Each

## Slide 6: Sanitary Sewer - Gravity Pipe Size Breakdown
Chart: 
| 6 inch | 8 inch | 10 inch | 12 inch | 15 inch | 18 inch
Percent | 0.0074858 | 0.89199 | 0.032044 | 0.064962 | 0.0011143 | 0.0024051
Size | 0 | 0 | 0 | 0 | 0 | 0
Length (Feet) | 437.8212 | 52169.5093 | 1874.1322 | 3799.4448 | 65.1703 | 140.6662

## Slide 7: Sanitary Sewer Pipe Material Breakdown
Chart: Sanitary Sewer - Gravity Pipe Material Breakdown
| AC | PVC | RPM | VCP
Percent | 0.0032819 | 0.41792 | 0.034989 | 0.54381
Material | 0 | 0 | 0 | 0
Length (Feet) | 191.9452 | 24442.8673 | 2046.4201 | 31805.5114

## Slide 8: Criticality of Assets
Probability of Failure (PoF) - Rated from 0 to 5
  PACP Overall Quick Rating
  Age-based Assumed Condition
Consequence of Failure (CoF) – Rated from 1-5
  Manually Assigned
Business Risk (BR) – Rated from 1-25
  0-8 (Not Critical)
  8-16 (Important but not Critical)
  16-25 (Critical)

## Slide 9: Business Risk
Table 1.4 - Risk Assessment |  |  |  | 
Asset Type | Business Risk |  |  | 
 | 0-8 | 8-16 | 16-25 | Totals
Sanitary Sewer (Feet) | 52,753 | 5,119 | 615 | 58,487
Manholes (Each) | 234 | 11 | 0 | 245

## Slide 10: Existing Gravity Sewer Collection Piping
Table 3.1 Existing Gravity Sewer Collection Piping |  |  |  |  | 
Material (feet) | Material (feet) |  |  |  | 
4 inch | AC | PVC | RPM | VCP | Totals
6 inch |  |  |  | 438 | 438
8 inch | 192 | 20,504 | 821 | 30,653 | 52,170
10 inch |  | 584 | 575 | 715 | 1,874
12 inch |  | 3,149 | 650 |  | 3,799
15 inch |  | 65 |  |  | 65
18 inch |  | 141 |  |  | 141
Totals | 192 | 24,443 | 2,046 | 31,806 | 58,487

## Slide 11: Condition Assessment
Table 7.1 - Condition Assessment | 
Ratings Index | Description
5 | Asset Unserviceable - Over 50% of asset requires replacement
4 | Significant deterioration - significant renewal/upgrade required (20 -40%)
3 | Moderate deterioration - Significant maintenance required (10 -20%)
2 | Minor Deterioration - Minor maintenance required (5%)
1 | New or Excellent Condition - Only normal maintenance required

## Slide 12: Probability of Failure (PoF)
Table 7.2 - Probability of Failure | 
Performance Rating | Description
5 | Imminent - Likely to occur in the life of the item
4 | Probable - Will occur several times in the life of an item
3 | Occasional - Likely to occur some- time in the life of an item
2 | Remote - Unlikely but possible to occur in the life of an item
1 | Improbable - So unlikely, it can be assumed occurrence may not be experienced

## Slide 13: Consequence of Failure (CoF)
Table 7.3 - Consequence of Failure | 
Performance Rating | Description
5 | Catastrophic disruption
4 | Major disruption
3 | Moderate disruption
2 | Minor disruption
1 | Insignificant disruption

## Slide 14: Manhole Business Risk
Table 7.4 - Risk Assessment |  |  |  | 
Asset Type | Business Risk |  |  | 
 | 0-8 | 8-16 | 16-25 | Totals
Manholes (Each) | 234 | 11 | 0 | 245

## Slide 15: Gravity Sewer Business Risk
Table 7.5 - Risk Assessment |  |  |  | 
Asset Type | Business Risk |  |  | 
 | 0-8 | 8-16 | 16-25 | Totals
Sanitary Sewer (Feet) | 52,753 | 5,119 | 615 | 58,487

## Slide 16: Pump Station/Force Main Business Risk
Table 7.6 Risk Assessment |  |  |  | 
Pump/Lift Station | Force Main Diameter (inch) | Force Main Material | Force Main Length (feet) | Rating
No. 1 | 12 | FPVC | 4,717 | 1
No. 3 | 4 | Ductile Iron | 260 | 2
No. 4 | 4 | HDPE | 485 | 2
No. 5 | 4 | HDPE | 430 | 2

## Slide 17: Capital Improvement Plan
Capital Projects scheduled to be constructed in 2023
MACP and PACP Rehabilitation Program
Capital Projects scheduled to be constructed within ten years

## Slide 18: Capital Projects scheduled to be constructed in 2023

## Slide 19: MACP and PACP Rehabilitation Program

## Slide 20: Capital Projects scheduled to be constructed within ten years

## Slide 21: OM&R Budget and Rate Sufficiency

## Slide 22: GIS Mapping and Ongoing Data Management